## SDR1
SECTION 6.0 |  |  | SCHEDULE OF DESIGN REQUIREMENTS
6.1 | PROJECT INFORMATION
6.1.1 | General
All work under this Specification shall subject to the requirements stated herein all of which
shall be included and form part of this Contract.
The Sub-Contractor shall include all permits and inspection fees payable to all Authorities, overtime payments and all other charges and costs necessary to complete the work within the submitted Sub-Contractor programme.
The Sub-Contractor must familiarize himself with the existing site condition and has taken
into consideration the working space, mean of access, storage and materials disposal.
6.1.2 | Scope of Work
The Sub-Contractor shall supply labour, materials, equipment and services; deliver, complete the new installation, setting the work for testing and commissioning for the complete Air-Conditioning and Ventilation Systems as a part of this contract.
The work to be performed under this part shall include but not necessarily be limited to the
following scope of work.
| (a) | Supply, Deliver and Install
|  | (i) |  | Complete Precision Air Conditioning Unit air-conditioning system including
condensing unit, indoor unit, control panel, piping,wiring etc;
|  | (ii) |  | Mechanical Ventilation Exhaust system and
|  | (iii) |  | Ductworks and insulation for air conditioning and ventilation system.
|  | for functioning |  |  | ( Name of project ) |  |  | , as stated in this specification and in
accordance with the details shown in the accompanying tender drawings.
| (b) | Submission of shop drawings, as-installed drawings, test results, maintenance
manuals, operating instructions of the services and the installed equipment.
| (c) | Guarantee and monthly service of the complete installed system for a period of
twelve (12) months after handing over to the Jabatan Kerja Raya, in good operating
condition.
| (d) | All hacking, coring and making good of works to be included in the project costing.
6.2 | DESIGN INFORMATION
6.2.1 | General
The following design conditions have been incorporated for this project:
Inside Design Conditions
The room air conditions shall be maintained at 74±1ºF DB and 55% ±5% RH.
Outside Ambient Conditions
Design calculations have been based on outside condition of 95ºF DB and 83ºF WB.
Fresh Air Ventilation
Unless otherwise specified, the amount of fresh air for ventilation purposes shall be taken
as not less than 15 cfm per person or not less than one complete air change per hour,
whichever is the greater.
Sensors and Controls
Sensors and controls are employed to facilitate operation and maintenance of the system.
6.2.2 | Ventilation and Exhaust System
Where ventilation is required, the Schedule of Design Requirement and/or Tender Drawings will indicate the number of ventilation fans, type, size, electrical characteristics and rate of air flow against a static head. The fan shall be inclusive of starters, switch fuses and wiring from the fan to the control panel. The static head given must commensurate to the fan performance required. The static head given in the Schedule of Design Requirement is only a guide and calculated based on design condition.
The enclosure being ventilated shall be adequately protected from infiltration of rain through the fan by the provision of suitable aluminium hood and gravity shutters. For those fans that are serving areas with fire suppression system protection, it shall be set to cut off simultaneously when the agent is discharged.
6.3 | SCHEDULE OF TECHNICAL EQUIPMENT
6.3.1 | Precision Air Conditioning Units
| a) | No. of Condensing Unit | [5 empty] | : | nos
| b) | No. of Indoor Unit | [5 empty] | : | nos
| c) | PVC Drain Pan (insulated and to nearest drain) | [5 empty] | : | lot
|  | Switchboard c/w starters, isolators, controls | [5 empty] | : | nos
voltmeters, ammeters, single phasing device,
indicating lights, auxilliary contactors, power
correction devices, etc..
| d) | Remote control panel | [5 empty] | : | nos
| e) | Piping | [5 empty] | : | nos
| f) | Pipe Jointing | [5 empty] | : | nos
| g) | Pipe Insulation | [5 empty] | : | nos
6.3.2 | Pipe Insulation
| (a) | Refrigerant Pipe |  |  |  | : | Pre-Insulated PU Injected Pipe
6.3.3 | Pipe Jointing (≤ 65 mm diameter)
| (a) | Refrigerant Pipe |  |  |  | : | Welded

## SDR2
6.3.2 | Precision Air Conditioning Unit
Unit Number |  | Location | Type | Minimum Total Cooling (Btu/hr) | Minimum Airflow (cfm) |  | Outdoor Unit Total Capacity (Btu/hr)
`

## TABC
6.4 | SCHEDULE OF TABC REQUIREMENTS
6.4.1 | Pre Delivery Stage
No. | Inspection / Test Name | Scope | Responsibility | Price (RM)
1 | Switchboard Test | Above 600A rated switchboard as per Section 4; 1.2.1.1 Table 2 | Contractor and Suruhanjaya Tenaga Certified Switchboard's manufacturer. All results must be certified by Competent Person as in Electricity Regulations 1994.
6.4.2 | Delivery Stage
No. | Inspection / Test Name | Scope | Responsibility | Price (RM)
2 | Visual inspection | All delivered material and equipment to site inspected against technical specification, approved materials and good physical conditions. | Contractor
6.4.3 | Installation Stage
No. | Inspection / Test Name | Scope | Responsibility | Price (RM)
3 | Visual inspection | All installation subjected to technical specifications and drawings. | Contractor
4 | Refrigerant Leak Test | Refrigerant pipe & Equipment | Contractor
5 | Refrigerant Charge Test | PACU Unit | Contractor
6 | Purging/Flushing | Refrigerant pipe and drain pipe | Contractor
7 | Cable Continuity Test | All power cabling | Contractor
8 | Pipe gradient test | All condensate drain pipe | Contractor
6.4.4 | Functional Performance Stage
No. | Inspection / Test Name | Scope | Responsibility | Price (RM)
Pre Functional Performance Test
9 | Accuracy Test | Accuracy test for all field gauges, tranducers, sensors and meters. | Contractor
Precision Air Conditionig Unit (PACU)
10 | PACU General inspection | All PACU Unit | Contractor
11 | Cooling Coil Performance/COP test | All PACU Unit | Contractor and results verified by manufacturer
12 | PACU Refrigerant High/Low Pressure Protection Test | All PACU Unit | Contractor
13 | PACU Control test | All PACU Unit | Contractor
14 | Noise Level Test | All PACU Unit | Contractor
Switchboard and Power Supply Test
15 | Switchboard General Inspection | All switchboard | Contractor and results verified by electrical competent person.
16 | Power Supply Test | All switchboard | Contractor and results verified by electrical competent person.
17 | Overcurrent and Earth Fault Protection | All switchboard | Contractor and results verified by electrical competent person.
Air Distribution Test
18 | Room Condition Test | Spot measurements of temperature, humidity and air velocity using sling psychrometer and anemometer at anticipated peak and minimum cooling load period as per S.O instructions. Logged data for critical areas as per Section 4. | Contractor
19 | Pressurisation test | Zone where differential pressure requirements are specified. | Contractor