| CAWANGAN KEJURUTERAAN MEKANIKAL |  | BORANG FF- SKM 2 - 2009 |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | CHECKLIST OF ACCEPTANCE CRITERIA |  |  |  |
|  |  | SERVICES : FIRE PROTECTION SYSTEM |  |  |  |
|  |  | PROJECT NAME : |  |  |  |
|  |  | FILE NO : |  |  |  |
| ACCEPTANCE CRITERIA FOR INSTALLATION OF CLEAN AGENT SYSTEM |  |  |  |  |  |
| NO | ITEMS | CRITERIA | (√) / (X) | DATE / INITIAL | REMARKS |
| 1 | DRAWINGS & DOCUMENTS |  |  |  |  |
| a. | Working drawings | Provided and approved before the system installation is carried out |  |  |  |
|  |  | Coordination with other system/dicipline |  |  |  |
| b. | Contract document/Copy of Technical Specification, Design Requirement and Schedule of Technical Offered | Provided. If no, please specify. |  |  |  |
| 2 | TECHNICAL CHECKLIST |  |  |  |  |
| 2.1 | Cylinder |  |  |  |  |
| a. | Capacity & quantity | Provided |  |  |  |
| 2.2 | Pipework |  |  |  |  |
| a. | Material | Carbon Steel Sch 80 - >20mm |  |  |  |
|  |  | Carbon Steel Sch 40 - <20mm |  |  |  |
| b. | Joint | Thread tapings |  |  |  |
| c. | Pipes passing through walls/floors | Through sleeves |  |  |  |
| 2.3 | Control Panel |  |  |  |  |
| a. | Battery compartment | Place in lockable box. |  |  |  |
| b. | Control switch | Mounted on black perspex |  |  |  |
| c. | Indicating Light | Provided |  |  |  |
| 2.4 | Heat Detector |  |  |  |  |
| a. | Installation | Provided |  |  |  |
| 2.5 | Smoke Detector |  |  |  |  |
| a. | Installation | Provided |  |  |  |
| 2.6 | Remote Manual Control |  |  |  |  |
| a. | Type | Manual pull box and of the ‘Break glass’ type |  |  |  |
| 2.7 | Audible Alarm |  |  |  |  |
| a. | Type | Electrically operated dome-type alarm bells |  |  |  |
| 2.8 | Fire Curtains |  |  |  |  |
| a. | Material | Glass fiber |  |  |  |
| b. | Assembled | Rolled up, weighed and held by mild steel mounting brackets and cable guides c/w tripping device and 24V D.C. actuator for each piece of curtain |  |  |  |
| 2.9 | Battery |  |  |  |  |
| a. | Installation and location | Provided |  |  |  |
| b. | Type | Nickel Cadmium |  |  |  |
| 2.10 | Battery Charger |  |  |  |  |
| a. | Installation and location | Provided |  |  |  |
| 2.11 | Warning/Flashing Light |  |  |  |  |
| a. | Type | Strobe/Beacon |  |  |  |
| b. | Installation and location | Provided |  |  |  |
| 2.12 | Wiring |  |  |  |  |
| a. | Location | Provided as per working drawing |  |  |  |
| b. | Installation | Run in conduit |  |  |  |

NOTES :

√  -   Comply to specification/drawings (Acceptable)

X  -   Not Comply to specification/drawings (Not Acceptable)

COMMENTS :

Inspected by : 	Verified by :

……………………………………….	…………………………………………. Name : 	Name :

Designation :	Designation : Date : 	Date :