## SDR1
SECTION 6.0 |  |  | SCHEDULE OF DESIGN REQUIREMENTS
6.1 | PROJECT INFORMATION
6.1.1 | General
All work under this Specification shall subject to the requirements stated herein all of which shall be included and form part of this Contract.
The Sub-Contractor shall include all permits and inspection fees payable to all Authorities, overtime payments and all other charges and costs necessary to complete the work within the submitted Sub-Contractor programme.
The Sub-Contractor must familiarize himself with the existing site condition and has taken
into consideration the working space, mean of access, storage and materials disposal.
6.1.2 | Scope of Work
The Sub-Contractor shall supply labour, materials, equipment and services; deliver, complete the new installation, setting the work for testing and commissioning for the complete Air-Conditioning and Ventilation Systems as a part of this contract.
The work to be performed under this part shall include but not necessarily be limited to the
following scope of work.
| (a) | Supply, Deliver and Install
|  | (i) |  | Complete Air Cooled Package air-conditioning system including package unit,
Fan coil unit (FCU), control panel, piping,wiring etc;
|  | (ii) |  | Mechanical Ventilation Exhaust system and
|  | (iii) |  | Ductworks and insulation for air conditioning and ventilation system.
|  | (iii) |  | Ductworks and insulation for air conditioning and ventilation system.
|  | for functioning |  |  | ( Name of project ) | , as stated in this specification and in
accordance with the details shown in the accompanying tender drawings.
| (b) | Submission of shop drawings, as-installed drawings, test results, maintenance
manuals, operating instructions of the services and the installed equipment.
| (c) | Guarantee and monthly service of the complete installed system for a period of
twelve (12) months after handing over to the Jabatan Kerja Raya, in good operating
condition.
| (d) | All hacking, coring and making good of works to be included in the project costing.
6.2 | DESIGN INFORMATION
6.2.1 | General
The following design conditions have been incorporated for this project:
Inside Design Conditions
The room air conditions shall be maintained at 74±1ºF DB and 55% ±5% RH.
Outside Ambient Conditions
Design calculations have been based on outside condition of 95ºF DB and 83ºF WB.
Fresh Air Ventilation
Unless otherwise specified, the amount of fresh air for ventilation purposes shall be taken
as not less than 15 cfm per person or not less than one complete air change per hour,
whichever is the greater.
Sensors and Controls
Sensors and controls are employed to facilitate operation and maintenance of the system.
6.2.2 | Ventilation and Exhaust System
Where ventilation is required, the Schedule of Design Requirement and/or Tender Drawings will indicate the number of ventilation fans, type, size, electrical characteristics and rate of air flow against a static head. The fan shall be inclusive of starters, switch fuses and wiring from the fan to the control panel. The static head given must commensurate to the fan performance required. The static head given in the Schedule of Design Requirement is only a guide and calculated based on design condition.
The enclosure being ventilated shall be adequately protected from infiltration of rain through
the fan by the provision of suitable aluminium hood and gravity shutters. For those fans that
are serving areas with fire suppression system protection, it shall be set to cut off
simultaneously when the agent is discharged.
6.2.3 | Control of Indoor Air Quality
The control of indoor air quality is required to enhance the quality of indoor air that the AHU/FCU serves to meet the room condition as per IAQ requirement.
6.3 | SCHEDULE OF TECHNICAL EQUIPMENT
6.3.1 | Air Cooled Package Units
| a) | No. of ACPU or AHU |  |  |  | : | nos
| b) | Supply Duct c/w Insulation |  |  |  | : | lot
| c) | Return Duct c/w Insulation |  |  |  | : | lot
| d) | Supply air grilles c/w acessories |  |  |  | : | lot
| e) | Return air grilles c/w acessories |  |  |  | : | lot
| f) | PVC Drain Pan (insulated and to nearest drain) |  |  |  | : | lot
| g) | Switchboard c/w starters, isolators, controls |  |  |  | : | nos
|  | voltmeters, ammeters, single phasing device, |  |  |  | :
|  | indicating lights, auxilliary contactors, power |  |  |  | :
|  | correction devices, etc.. |  |  |  | :
| h) | Remote control panel for AHU |  |  |  | : | nos

## SDR2
6.3.2 | Air Cooled Package Unit
Unit Number |  | Cooling Capacity (Btu/hr) |  |  |  | Grand Total | TR | Fresh Air (cfm) | Supply Air (cfm) | Air Entering (⁰C) |  | Air Leaving (⁰C) |  |  | Fan Static | Remarks
|  | Sensible | Latent | Outdoor Air Heat
|  | ERSH | ERLH | Latent | Sensible |  |  |  |  | DB | WB | DB |  | WB
`

## SDR3
6.3.6 | Material of Ductwork
| (a) | Supply Duct | : |  | Sheet metal duct/ Pre fabricated duct
| (b) | Return Duct | : |  | Sheet metal duct/ Pre fabricated duct
6.3.7 | External and Internal Insulation of Ductwork (Sheet Metal)
| (a) | Supply Duct (External) | : |  | Fiberglass/ PE Foam/ Closed Cell Nitrile Rubber
| (b) | Return Duct (External) | : |  | Fiberglass/ PE Foam/ Closed Cell Nitrile Rubber
| (c) | Supply Duct (Internal) | : |  | Fiberglass/ Open Cell PU Foam
6.3.7 | Internal Insulation of Ductwork (Pre-Insulated)
| (a) | Silencer (Location) | : |  | Provided at main air supply duct after the first fire
damper insulation at AHU room.
| (b) | Supply Duct (Internal) | : |  | Open Cell PU Foam
6.3.9 | Hanger System for Bases and Plenums, Registers, Diffusers and Grilles
| Diffusion Equipment |  | : |  | Bases and plenums, registers, diffusers and
grilles
| Hanger type |  | : |  | Adjustable 1.2 mm diameter suspension rod
complete with clip type (refer tender drawing)
| Quantity |  | : |  | 1 Lot
6.3.10 | Pipe Insulation
| (a) | Refrigerant Pipe | : |  | 50 mm Closed Cell Nitrile Rubber
| (b) | Underground pipe | : |  | High density polyethylene (HDPE) tube conforming
|  | (Jacketing) |  |  | to ASTM D 1248, Type III, Category 5, Class C and
6.3.11 | Indoor Air Quality Control System
| (a) | Type of IAQ Control System |  | : |  | AHU/FCU Cooling Coil and Fins Treatment
OR
Ultraviolet Air Purifier System
`

## TABC
6.4 | SCHEDULE OF TABC REQUIREMENTS
6.4.1 | Pre Delivery Stage
No. | Inspection / Test Name | Scope | Responsibility
1 | Switchboard Test | Above 600A rated switchboard as per Section 4; 1.2.1.1 Table 2 | Contractor and Suruhanjaya Tenaga Certified Switchboard's manufacturer. All results must be certified by Competent Person as in Electricity Regulations 1994.
6.4.2 | Delivery Stage
Bil. | Inspection / Test Name | Scope | Responsibility
2 | Visual inspection | All delivered material and equipment to site inspected against technical specification, approved materials and good physical conditions. | Contractor
6.4.3 | Installation Stage
Bil. | Inspection / Test Name | Scope | Responsibility
3 | Visual inspection | All installation subjected to technical specifications and drawings. | Contractor
4 | Refrigerant Leak Test | Refrigerant pipe & Equipment | Contractor
5 | Refrigerant Charge Test | ACPU | Contractor
6 | Purging/Flushing | Refrigerant pipe and drain pipe | Contractor
7 | Duct Leak test | All ductwork operating at and above 750 Pa (3.0 in.wg) | Contractor
8 | LV Motors, Switch Gears and Cabling Insulation Test | All LV Motors, Switch Gears and power cabling | Contractor
9 | Cable Continuity Test | All power cabling | Contractor
10 | Pipe gradient test | All condensate drain pipe | Contractor
6.4.4 | Functional Performance Stage
Bil. | Inspection / Test Name | Scope | Responsibility
Pre Functional Performance Test
11 | Air balancing | Air balancing for all supply, return, exhaust and fresh air duct. | Contractor
12 | Accuracy Test | Accuracy test for all field gauges, tranducers, sensors and meters. | Contractor
Air Cooled Package Unit (ACPU)
13 | ACPU General inspection | All ACPU Unit | Contractor
14 | Refrigerant Piping Inspection | All ACPU Unit | Contractor
15 | Fan Volumetric Air Flow Test | All ACPU Unit | Contractor
16 | Cooling Coil Performance/COP test | All ACPU Unit | Contractor and results verified by manufacturer
17 | ACPU Refrigerant High/Low Pressure Protection Test | All ACPU Unit | Contractor
18 | ACPU Control test | All ACPU Unit | Contractor
19 | Noise Level Test | All ACPU Unit | Contractor
Switchboard and Power Supply Test
20 | Switchboard General Inspection | All switchboard | Contractor and results verified by electrical competent person.
21 | Power Supply Test | All switchboard | Contractor and results verified by electrical competent person.
22 | Overcurrent and Earth Fault Protection | All switchboard | Contractor and results verified by electrical competent person.
Air Distribution Test
23 | Room Condition Test | Spot measurements of temperature, humidity and air velocity using sling psychrometer and anemometer at anticipated peak and minimum cooling load period as per S.O instructions. Logged data for critical areas as per Section 4. | Contractor
24 | Pressurisation test | Zone where differential pressure requirements are specified. | Contractor
25 | Duct Condensation Inspection | All Ductwork | Contractor
Mechanical Ventilation Test
26 | Fan General Inspection | All mechanical ventilation fan. | Contractor
27 | Fan Volumetric Air Flow test | All mechanical ventilation fan. | Contractor
28 | Fan Control test | All mechanical ventilation fan. | Contractor
29 | Noise Level Test | All mechanical ventilation fan. | Contractor