| CAWANGAN KEJURUTERAAN MEKANIKAL |  | BORANG FF- SKM 2 - 2009 |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | CHECKLIST OF ACCEPTANCE CRITERIA |  |  |  |
|  |  | SERVICES : FIRE PROTECTION SYSTEM |  |  |  |
|  |  | PROJECT NAME : |  |  |  |
|  |  | FILE NO : |  |  |  |
| ACCEPTANCE CRITERIA FOR INSTALLATION OF CARBON DIOXIDE EXTINGUISHING SYSTEM |  |  |  |  |  |
| NO | ITEMS | CRITERIA | (√) / (X) | DATE / INITIAL | REMARKS |
| 1 | DRAWINGS & DOCUMENTS |  |  |  |  |
| a. | Working drawings | Provided and approved before the system installation is carried out |  |  |  |
|  |  | Coordination with other system/dicipline |  |  |  |
| b. | Contract document/Copy of Technical Specification, Design Requirement and Schedule of Technical Offered | Provided. If no, please specify. |  |  |  |
| 2 | TECHNICAL CHECKLIST |  |  |  |  |
| 2.1 | Storage Cylinder |  |  |  |  |
| a. | Type of cylinder | Rechargeable containers |  |  |  |
| 2.2 | Detector Head |  |  |  |  |
| a. | Detector head installation | 1. Using 1.5mm2 PVC grade cables in be run in separate conduit and shall not G.I conduit |  |  |  |
|  |  | 2. Detector and actuating circuits shallshare the same conduit with other wiring. |  |  |  |
|  |  | 3. Min. size of G.I conduit - 19 mm dia. |  |  |  |
| 2.3 | Smoke Detector |  |  |  |  |
| a. | Installation and location | Provided |  |  |  |
| 2.4 | Heat Detector |  |  |  |  |
| a. | Installation and location | Provided |  |  |  |
| 2.5 | Audible Alarms |  |  |  |  |
| a. | Type | Electrically operated dome-type alarm bells |  |  |  |
| b. | Material | Pressed steel gong |  |  |  |
| c. | Gong size | Minimum 150mm |  |  |  |
| 2.6 | Control Panel |  |  |  |  |
| a. | Battery compartment | Place in lockable box. |  |  |  |
| b. | Control switch | Mounted on black perspex |  |  |  |
| c. | Indicating Light | Provided |  |  |  |
| 2.7 | Battery |  |  |  |  |
| a. | Type | Nickel Cadmium rechargeable type |  |  |  |
| b. | Charger | Provided |  |  |  |
| c. | Installation and location | Provided |  |  |  |
| 2.8 | Piping |  |  |  |  |
| a. | Material | Galvanised Steel Class C |  |  |  |
| b. | Flanges | 1. Type - Raised face |  |  |  |
|  |  | 2. Material - Forged carbon steel |  |  |  |
| c. | Fittings for closed section of pipe ≤ 40mm | Forged steel/screwed |  |  |  |
| d. | Fittings for open ended pipe ≤20mm | Screwed |  |  |  |
| 2.9 | Safety Devices |  |  |  |  |
| a. | Installation and location | Provided |  |  |  |
| 2.10 | Ventilation Fans |  |  |  |  |
| a. | Fan wiring | Direct from fan to the control panel |  |  |  |

| NO | ITEMS | CRITERIA | (√) / (X) | DATE / INITIAL | REMARKS |
| --- | --- | --- | --- | --- | --- |
| 2.11 | Wiring |  |  |  |  |
| a. | Material | 1. PVC insulated cables |  |  |  |
|  |  | 2. Enclosed in galvanised metal conduits/trunking |  |  |  |
| b. | Conduits | Size - min. 19mm |  |  |  |
| c. | Min. cable size | 1. Detectors and control wire - 1.5mm2 |  |  |  |
|  |  | 2. Alarm bell and flashing light - 4mm2 |  |  |  |
| d. | Installation and location | Provided as per drawing |  |  |  |
| 2.12 | Gravity Shutters |  |  |  |  |
| a. | Material | Glass fiber |  |  |  |
| b. | Assembled | Rolled up, weighed and held by mild steel mounting brackets and cable guides c/w tripping device and 24V D.C. actuator for each piece of curtain |  |  |  |
| NOTES : √ - Comply to specification/drawings (Acceptable) X - Not Comply to specification/drawings (Not Acceptable) |  |  |  |  |  |
| COMMENTS : Inspected by : Verified by : ………………………………………. …………………………………………. Name : Name : Designation : Designation : Date : Date : |  |  |  |  |  |