## SDR1
SECTION 6.0 |  |  |  | SCHEDULE OF DESIGN REQUIREMENTS
6.1 | PROJECT INFORMATION
6.1.1 | General
All work under this Specification shall subject to the requirements stated herein all of which
shall be included and form part of this Contract.
The Sub-Contractor shall include all permits and inspection fees payable to all Authorities, overtime payments and all other charges and costs necessary to complete the work within the submitted Sub-Contractor programme.
The Sub-Contractor must familiarize himself with the existing site condition and has taken
into consideration the working space, mean of access, storage and materials disposal.
6.1.2 | Scope of Work
The Sub-Contractor shall supply labour, materials, equipment and services; deliver, complete the new installation, setting the work for testing and commissioning for the complete Air-Conditioning and Ventilation Systems as a part of this contract.
The work to be performed under this part shall include but not necessarily be limited to the
following scope of work.
| (a) |  | Supply, Deliver and Install
|  |  | (i) |  | Complete Water Cooled Chiller air-conditioning system including chillers,
pumps, cooling tower, make up tank, expansion tank, air handling unit (AHU),
Fan coil unit (FCU), control panel, piping, wiring etc;
|  |  | (ii) |  | Mechanical Ventilation Exhaust system and
iii
|  |  | (iii) |  | Ductworks and insulation for air conditioning and ventilation system.
|  |  | for functioning |  |  | ( Name of project ) | , as stated in this specification and in
accordance with the details shown in the accompanying tender drawings.
| (b) |  | Submission of shop drawings, as-installed drawings, test results, maintenance
manuals, operating instructions of the services and the installed equipment.
| (c) |  | Guarantee and monthly service of the complete installed system for a period of
twelve (12) months after handing over to the Jabatan Kerja Raya, in good operating
condition.
| (d) |  | All hacking, coring and making good of works to be included in the project costing.
6.2 | DESIGN INFORMATION
6.2.1 | General
The following design conditions have been incorporated for this project:
Inside Design Conditions
The room air conditions shall be maintained at 74±1ºF DB and 55% ±5% RH.
Outside Ambient Conditions
Design calculations have been based on outside condition of 95ºF DB and 83ºF WB.
Fresh Air Ventilation
Unless otherwise specified, the amount of fresh air for ventilation purposes shall be taken
as not less than 15 cfm per person or not less than one complete air change per hour,
whichever is the greater.
Chilled Water System
The chiller shall be capable to chill the water through a range of 10ºF (from 54ºF to 44ºF).
Condenser Water System
The heat rejection equipment shall be capable to cool the condenser water through 10ºF
(from 97.5ºF to 87.5ºF).
Sensors and Controls
Sensors and controls are employed to facilitate operation and maintenance of the system.
6.2.2 | Ventilation and Exhaust System
Where ventilation is required, the Schedule of Design Requirement and/or Tender Drawings will indicate the number of ventilation fans, type, size, electrical characteristics and rate of air flow against a static head. The fan shall be inclusive of starters, switch fuses and wiring from the fan to the control panel. The static head given must commensurate to the fan performance required. The static head given in the Schedule of Design Requirement is only a guide and calculated based on design condition.
The enclosure being ventilated shall be adequately protected from infiltration of rain through the fan by the provision of suitable aluminium hood and gravity shutters. For those fans that are serving areas with fire suppression system protection, it shall be set to cut off simultaneously when the agent is discharged.
6.2.3 | Piping
All pipeworks for Chilled Water shall be of factory pre-insulated type.
All pipeworks shall be balanced by employing Balancing Valves and other fittings necessary to attain this. All pipeworks shall be painted with colours as described under Section 3.
The calculated system head for all the chilled water pumps and the condenser water pumps are indicated only as a guide in selecting the equipment for tender. The Sub Contractor shall ensure that the installed pumps shall meet all required installed system head. The Sub Contractor shall provide detailed pressure drop calculations for the installed chilled water and condenser water system.
6.2.4 | Control of Indoor Air Quality
The control of indoor air quality is required to enhance the quality of indoor air that the AHU/FCU serves to meet the room condition as per IAQ requirement.
`
6.3 | SCHEDULE OF TECHNICAL EQUIPMENT
6.3.1 | Water Cooled Chilled Units
| a) |  | No. of chiller |  |  |  | : |  | nos
| b) |  | Chiller capacity (each) |  |  |  | : |  | TR (each)
| c) |  | Chilled water quantity (minimum) |  |  |  | : |  | usgpm (each)
| d) |  | Fouling Factor |  |  |  | :
| e) |  | Entering chilled water temp. |  |  |  | : | 54oF
| f) |  | Leaving chilled water temp. |  |  |  | : | 44oF
| g) |  | Cooler pass arrangement |  |  |  | : | pass
| h) |  | Maximun pressure drop in cooler |  |  |  | : |  | ft.w.g
| i) |  | Condenser water quantity (minimum) |  |  |  | : |  | usgpm
| j) |  | Entering condenser water temp. |  |  |  | : | 87.5oF
| k) |  | Leaving condenser water temp. |  |  |  | : | 97.5oF
| l) |  | Condenser pass arrangement |  |  |  | : | pass
| m) |  | Maximun pressure drop in condenser |  |  |  | : |  | ft.w.g
| n) |  | Motor characteristics |  |  |  | : |  | V (+10%, -6%) / 3Ph / 50Hz
| o) |  | Type of Controller |  |  |  | : | Soft Starter
| p) |  | Kw per ton at full load |  |  |  | : |  | kW/ton
| q) |  | Type of compressor |  |  |  | : | Screw / Centrifugal Type
| r) |  | Type of refrigerant |  |  |  | : | R134a
| s) |  | Minimun capacity loading |  |  |  | :
Note :
Chiller shall have lead/ lag factory wired control
Complete Remote Monitoring Capabilities at Chiller System
To provide the Central Chiller Supervisory Control, Desktop PC, Original Software c/w accessories, Internet accessible handphone for remote monitoring purpose. Internet access fee shall be born by the Air Conditioing contractor for the period of defect liability.
The data remote monitoring shall utilized broadband facilties for hire real time data resolution.
6.3.2 | Chilled Water Pumps
| a) |  | Pump Quantity |  |  |  | : |  | nos
| b) |  | Pump Capacity (Each Pump) |  |  |  | : |  | usgpm
| c) |  | Pump Head @ 753 Usgpm (Each Pump) |  |  |  | : |  | ft.hd
| d) |  | Pump Efficiency,η :(not less than) |  |  |  | : |  | %
| e) |  | Pump type |  |  |  | : | Horizontal Split Casing/ End
Suction
| f) |  | Operating speed |  |  |  | : | ≤ 1500 rpm
| g) |  | Type of Pump Motor |  |  |  | : | HEM (EFF1/EFF2)
| h) |  | Pipe Diameter |  |  |  | : | mm
| i) |  | Motor insulation/ enclosure |  |  |  | :
| j) |  | Type of Controller |  |  |  | : | Soft Starter
Note :
All chilled water pipes shall be pre-insulated Galvanised Iron (G.I) Class 'C'
6.3.3 | Cooling Tower
| a) |  | Type of cooling tower |  |  |  | : | Cross flow/ Counter flow
| b) |  | Cooling Tower Quantity |  |  |  | : |  | nos
| c) |  | Minimum Capacity (each) |  |  |  | : |  | TR
| d) |  | Circulating water quantity |  |  |  | : |  | usgpm
| e) |  | Ambient Temp |  |  |  | : | 95oF / 80oF WB
| f) |  | Entering water temperature |  |  |  | : | 97.5oF
| g) |  | Leaving water temperature |  |  |  | : | 87.5oF
| h) |  | Type of blade/fan |  |  |  | :
6.3.4 | Condenser Water Pumps
| a) |  | Pump Quantity |  |  |  | : |  | nos
| b) |  | Pump Capacity (Each Pump) |  |  |  | : |  | usgpm
| c) |  | Pump Head @ 753 Usgpm (Each Pump) |  |  |  | : |  | ft.hd
| d) |  | Pump Efficiency,η :(not less than) |  |  |  | : |  | %
| e) |  | Pump type |  |  |  | : | Horizontal Split Casing/ End
Suction
| f) |  | Type of Pump Motor |  |  |  | : | HEM (EFF1/EFF2)
| g) |  | Pipe Diameter |  |  |  | : | mm
| h) |  | Motor insulation/ enclosure |  |  |  | :
| i) |  | Type of Controller |  |  |  | : | Soft Starter
Note :
All chilled water pipes shall be pre-insulated Galvanised Steel Class 'C'
6.3.5 | Water Tank
| a) |  | Make up water tank (1 no) minimum capacity |  |  |  | : |  | gallons
| b) |  | Material of water tanks |  |  |  | : | Hot Dipped Galvanised
| c) |  | Chilled Water Expansion Tank (1 no)
|  |  | minimum capacity |  |  |  | : |  | gallons
| d) |  | Material Insulation of tanks |  |  |  | : | Closed Cell Nitrile Rubber
| e) |  | Thickness of Insulation |  |  |  | : | 19 mm

## SDR2
6.3.6 | Air Handling Unit (AHU)
Unit Number |  | Location | Total Capacity | Sensible capacity |  | Supply Air |  | Fresh Air | Fan Total Static | AHU Type |  | Chilled Water flow
|  |  | (Btu/hr) | (Btu/hr) |  | (cfm) |  | (cfm) | Head (in.wg) |  |  | nominal usgpm
6.3.7 | AHU General
| a) | Primary Air Filters |  |  | : | 50 mm Flat Washable Filter
| b) | Air Filter Dust Spot Efficiency (atmospheric) |  |  | : | 30%
| c) | AHU Construction |  |  | : | Single Skin/ Double Skin
| d) | AHU Insulation |  |  | : | 50 mm Injected Rigid PU
| e) | Thermal Barrier/ Bridging |  |  | : | Class 2
| f) | Fan Type |  |  | :
| g) | External Static Pressure - AHU |  |  | : |  | in. wg
| h) | External Static Pressure - FCU |  |  | : |  | in. wg
`

## SDR3
6.3.8 | Material of Ductwork
| (a) |  | Supply Duct | : |  | Sheet metal duct/ Pre fabricated duct
| (b) |  | Return Duct | : |  | Sheet metal duct/ Pre fabricated duct
6.3.9 | External and Internal Insulation of Ductwork (Sheet Metal)
| (a) |  | Supply Duct (External) | : |  | Fiberglass/ PE Foam/ Closed Cell Nitrile Rubber
| (b) |  | Return Duct (External) | : |  | Fiberglass/ PE Foam/ Closed Cell Nitrile Rubber
| (c) |  | Supply Duct (Internal) | : |  | Fiberglass/ Open Cell PU Foam
6.3.10 | Internal Insulation of Ductwork (Pre-Insulated)
| (a) |  | Silencer (Location) | : |  | Provided at main air supply duct after the first fire
damper insulation at AHU room.
| (b) |  | Supply Duct (Internal) | : |  | Open Cell PU Foam
6.3.11 | Hanger System for Bases and Plenums, Registers, Diffusers and Grilles
| Diffusion Equipment |  |  | : |  | Bases and plenums, registers, diffusers and
grilles
| Hanger type |  |  | : |  | Adjustable 1.2 mm diameter suspension rod
complete with clip type (refer tender drawing)
| Quantity |  |  | : |  | 1 Lot
6.3.12 | Pipe Insulation - Chilled Water Pipe
| (a) |  | Supply Pipe (Insulation) | : |  | Pre-fabricated chilled water pipes
| (b) |  | Return Pipe (Insulation) | : |  | Pre-fabricated chilled water pipes
| (c) |  | Above ground pipe | : |  | 0.5 mm thick spiral formed lock seamed galvanised
|  |  | (Jacketing) |  |  | steel
| (d) |  | Underground pipe | : |  | High density polyethylene (HDPE) tube conforming
|  |  | (Jacketing) |  |  | to ASTM D 1248, Type III, Category 5, Class C and
Grade P34
6.3.13 | Pipe Jointing (≤ 65 mm diameter) - Chilled & Condenser Water Pipes
| (a) |  | Chilled Water Pipe | : |  | Flanged/ Welded/ Mechanical Joint
| (b) |  | Condenser Water Pipe | : |  | Flanged/ Welded/ Mechanical Joint
Note :
Note :
Pipe jointing for pipes 50 mm and below is using screw type joint.
6.3.14 | Indoor Air Quality Control System
| (a) |  | Type of IAQ Control System |  | : |  | AHU/FCU Cooling Coil and Fins Treatment
OR
Ultraviolet Air Purifier System
`

## TABC
6.4 | SCHEDULE OF TABC REQUIREMENTS
6.4.1 | Pre Delivery Stage
No. | Inspection / Test Name | Scope | Responsibility
1 | Chiller Factory Performance Test | All chiller | Contractor and results endorsed by manufacturer.
2 | Switchboard Factory Test | Above 600A rated switchboard as per Section 4; 1.2.1.2 Table 2. | Contractor and Suruhanjaya Tenaga Certified Switchboard's manufacturer. All results must be certified by Competent Person as in Electricity Regulations 1994.
6.4.2 | Delivery Stage
No. | Inspection / Test Name | Scope | Responsibility
3 | Visual Inspection | All delivered material and equipment to site inspected against technical specification, approved materials and good physical conditions. | Contractor
6.4.3 | Installation Stage
No. | Inspection / Test Name | Scope | Responsibility
4 | Visual Inspection | All installation shall be subjected to technical specifications and drawings. | Contractor
5 | Hydrostatic Pressure Test | All chilled and condenser water pipes. 1.5 times the normal working pressure of the system for period of 48 hours any leaks or deformations for the entire piping system. | Contractor
6 | Pipe Flushing and Water Quality Test | All chilled and condenser water pipe. 1st stage: Fresh water Online flushing (Debris removal) 2nd stage: Chemical flushing 3rd stage: Passivation (Corrosion control) 4th stage: Microbiological control (Biocide) | Contractor
7 | Duct Leak Test | All ductwork operating at and above 750 Pa (3.0 in.wg) | Contractor
8 | Duct Flushing | All ducts | Contractor
9 | LV Motors, Switch Gears and Cabling Insulation Test | All LV Motors, Switch Gears and power cabling | Contractor
10 | Cable Continuity Test | All power cabling | Contractor
11 | Pipe Gradient Test | All condensate drain pipe | Contractor
6.4.4 | Functional Performance Stage
No. | Inspection / Test Name | Scope | Responsibility
Pre Functional Performance Test
12 | Water Balancing | Water balancing for all chilled and condenser pipes. | Contractor
13 | Air Balancing | Air balancing for all supply, return, exhaust and fresh air duct.
14 | Accuracy Test | Accuracy test for all field gauges, tranducers, sensors and meters. | Contractor
Chiller Plant Test
15 | Chiller Plant General Inspection | All chiller | Contractor
16 | Chilled and Condenser Water Flow Test | All pumps | Contractor
17 | Chiller Plant Interlocking Test | Chiller plant | Contractor
18 | Chiller Low Flow Protection Test | All chiller | Contractor
19 | Chiller Low LCHW Protection Test | All chiller | Contractor
20 | Chiller High ECWT Protection Test | All chiller | Contractor
21 | Chiller Refrigerant Charge Adequacy Inspection | All chiller | Contractor
22 | Chiller Plant Noise Level Test | Chiller plant | Contractor
23 | Chiller Lead-Lag Control | Full system operating for three (3) consecutive days. | Contractor and results verified by vendor or manufacturer.
24 | Chiller Load Test | Full system operating for three (3) consecutive days. | Contractor and results verified by manufacturer.
25 | Cooling Tower Performance Test | Full system operating for three (3) consecutive days. | Contractor and results verified by manufacturer.
AHU Test
26 | AHU/FCU General Inspection | All AHU and FCU. | Contractor
27 | Total Volumetric Air Flow Test | All AHU and FCU. Time of test shall coincide with chiller load test period. | Contractor
28 | Cooling Coil Performance Test | All AHU and FCU. Time of test shall coincide with chiller load test period. | Contractor and results verified by manufacturer.
29 | AHU/FCU Control Test | All AHU and FCU. Time of test shall coincide with chiller load test period. | Contractor
30 | Noise Level Test | All AHU and FCU. | Contractor
Switchboard and Power Supply Test
31 | Switchboard General Inspection | All switchboard | Contractor and results verified by electrical competent person.
32 | Power Supply Test | All switchboard | Contractor and results verified by electrical competent person.
33 | Overcurrent and Earth Fault Protection | All switchboard | Contractor and results verified by electrical competent person.
Air Distribution Test
34 | Room Condition | Spot measurements of temperature, humidity and air velocity using sling psychrometer and anemometer at anticipated peak and minimum cooling load period as per S.O instructions. Logged data for critical areas as per Section 4; 1.2.4.5 (a). Time of test shall coincide with chiller load test period. | Contractor
35 | Pressurisation Test | Zone where differential pressure requirements are specified. | Contractor
36 | Duct Condensation Inspection | All air conditioning supply and return duct. | Contractor
Mechanical Ventilation Test
37 | Fan General Inspection | All mechanical ventilation fan. | Contractor
38 | Fan Volumetric Air Flow Test | All ducted mechanical ventilation fan. | Contractor
39 | Fan Control test | All mechanical ventilation fan. | Contractor
40 | Noise Level Test | All mechanical ventilation fan. | Contractor