## Slide 1: KURSUS REKABENTUK PEMASANGAN ELEKTRIK VOLTAN RENDAH (LANJUTAN) 27 & 28 Julai 2021
Ir. Siti Nor Binti Hassan
JEPK UPRBA2
CKE IBU PEJABAT

## Slide 2: Spesifikasi CKE
Sehingga Julai 2021 terdapat 41 bilangan Spesifikasi CKE (L-S1 hingga L-S41)
Terdapat 20 bilangan Spesifikasi CKE tersenarai dalam J-Pedia iaitu L-S1, L-S2, L-S3, L-S4, L-S5, L-S6, L-S9, L-S10, L-S11, L-S12, L-S13, L-S14, L-S15, L-S17, L-S20, L-S26, L-S29, L-S30, L-S31 & L-S32
Manakala terdapat 21 bilangan Spesifikasi CKE masih dalam pembangunan/ pengemaskinian iaitu L-S7, L-S8, L-S16, L-S18, L-S19, L-S21, L-S22, L-S23, L-S24, L-S25, L-S27, L-S28, L-S33, L-S34, L-S35, L-S36, L-S37, L-S38, L-S39, L-S40 & L-S41

## Slide 3: SENARAI Spesifikasi CKE
Dalam J-Pedia
Bil | L-S | Specification For
1 | 1 | Low Voltage Internal Electrical Installation
2 | 2 | Low Voltage Automatic Power Factor Correction Equipment
3 | 3 | Low Voltage Underground Cable
4 | 4 | Low Voltage Overhead Line Distribution System
5 | 5 | Three Phase Generator Set
6 | 6 | Acoustic Treatment For Generator Room
7 | 9 | Lightning Protection System For Structures

## Slide 4: SENARAI Spesifikasi CKE
Dalam J-Pedia
Bil | L-S | Specification For
8 | 10 | 11kV Distribution Transformers
9 | 11 | 11kV Medium Voltage Oil Circuit Breaker
10 | 12 | 11kV High Voltage Ring-Main Unit Distribution Switchgear
11 | 13 | 11kV High Voltage Underground Cable
12 | 14 | 11kV SF6 Ring Main Unit
13 | 15 | 11kV Metal-Enclosed Switchgear
14 | 17 | 11kV Dry-Type Distribution Transformer

## Slide 5: SENARAI Spesifikasi CKE
Dalam J-Pedia
Bil | L-S | Specification For
15 | 20 | Road Lighting Installation
16 | 26 | Satellite Master Antenna Television (SMATV) & Master Antenna Television (MATV) System
17 | 29 | Electronic Access Control System
18 | 30 | Queue Management System
19 | 31 | Stage Curtain System
20 | 32 | Visual System

## Slide 6: SENARAI Spesifikasi CKE
Dalam pembangunan/pengemaskinian Jawatankuasa
Bil | L-S | Specification For
1 | 7 | Single Phase Diesel Generator Set
2 | 8 | Lightning Protection System (Using Stranded G.I. Wires)
3 | 16 | Telephone Installation
4 | 18 | Uninterruptible Power Supply (UPS)
5 | 19 | Traffic Signal
6 | 21 | Diagnostic Imaging Equipment (Medical Equipment)
7 | 22 | Operation Theatre Table (Medical Equipment)

## Slide 7: SENARAI Spesifikasi CKE
Dalam pembangunan/pengemaskinian Jawatankuasa
Bil | L-S | Specification For
8 | 23 | Surgical Light (Medical Equipment)
9 | 24 | 60 Hz Frequency Converter
10 | 25 | Three Phase 400 Hz Frequency Converter
11 | 27 | Public Address (PA) System
12 | 28 | Aeronautical Ground Lighting System (AGL)
13 | 33 | Sound Reinforcement System
14 | 34 | Conference System

## Slide 8: SENARAI Spesifikasi CKE
Dalam pembangunan/pengemaskinian Jawatankuasa
Bil | L-S | Specification For
15 | 35 | Navigation Light
16 | 36 | Nurse Call System
17 | 37 | Helipad
18 | 38 | ICT Networking System
19 | 39 | Closed Circuit Television (CCTV) System
20 | 40 | Fireman Intercom System
21 | 41 | Three Phase Canopy Genset

## Slide 9: Rekabentuk Terkini
Keperluan TNB terkini iaitu Ogos 2019 dalam Esah v3.1
  LVCT Ground Mounted TNB Meter Kiosk
  Direct Meter Board (Hardwood)
  Meter Panel (Group Metering)
Keperluan bilik meter setiap aras jika kuarters (high rise) melebihi ≥6 tingkat
Keperluan Feeder Pillar selepas LVCT Ground Mounted TNB Meter Kiosk ATAU
Keperluan Pre MSB (sebelah PE TNB)

## Slide 10: Rekabentuk Terkini
Penggunaan Kelengkapan Lampu LED :
  External Lighting
    Lampu Kawasan/Jalan, Lampu Pagar, Lampu Papan Tanda, Lampu Façade, LED Bulkhead
  Internal Lighting
    T8 LED, LED Downlight, High/Low Bay LED Luminaire

## Slide 11: Kriteria penting
  Internal Lighting – T8 LED
    Self-Ballasted Double Capped LED Lamp
    Barang Kawalan Suruhanjaya Tenaga
    Correlated Colour Temperature, CCT
      4000K
      5000K
    Safety Photobiological Class : Exempt Group
    ≤ 11W / ≤ 20W
    ≥ 840 lm / ≥ 1400 lm
    ≥ 70 lm/W / ≥ 80 lm/W
    Pasang SPD pada DB Lighting

## Slide 12: Kriteria penting
Internal Lighting – LED Downlight
  Diameter : 150mm / 200mm
  Mild Steel
  CCT : 4000K, 5000K
  Frosted Tampered Glass
  Safety Photobiological Class : Exempt Group
  ≤ 20W
  ≥ 850 lm (4000K) / ≥ 950 lm (5000K)
  ≥ 75 lm/W (4000K) / ≥ 75 lm/W (5000K)
  Pasang SPD pada DB Lighting

## Slide 13: Kriteria penting
External Lighting – LED
  CCT : 3000K
  CCT : 5000K/6500K untuk Lampu Papan Tanda/ Facade
  ≥ 100 lm/W
  IP 54
  Mesti pasang SPD dalam Service Door

## Slide 14: Kaedah Pengiraan bilangan lampu LED (INTERNAL)
Menggunakan Software DIALux
Mesti ada IES files dari Supplier/Manufacturer

## Slide 15: Kaedah Pengiraan bilangan lampu LED (EXTERNAL)
Menggunakan Software DIALux
Merujuk kepada Table 3 dan 5 dalam CIE 115 (Lighting of Roads For Motor And Pedestrian Traffic)
Perlu ada pengetahuan untuk menyemak keputusan simulasi DIALux

## Slide 16: Kaedah Pengiraan bilangan lampu LED (SPOrts court)
Rujuk BS EN 12193 (Light and Lighting : Sports Lighting) / Garis Panduan Dan Peraturan Bagi Perancangan Bangunan Edisi Tahun 2015 / FIFA
Menggunakan Software DIALux
Perlu ada pengetahuan untuk menyemak keputusan simulasi DIALux

## Slide 17: Reka bentuk instant water heater point
Wajib patuh kepada PPE 1994 Peraturan 36
Mengadakan 25A DP RCCB (10mA)
Pendawaian dari 63A DP RCCB (100mA) i.e lighting circuit
Menggunakan 25A Connection Unit (Dahulu 15A 3 pin SSO)

## Slide 18: Beban Mekanikal
Jadual untuk Motor Fire Fighting System
Jadual untuk Motor Sistem Air Condition
15 A 3 Pin sso untuk Air Cond ≤ 2.5hp / 1865W
≥ 2.5hp please select the suitable rating of SPN Isolator

## Slide 19: POWER FACTOR CORRECTION BOARD
Kaedah untuk mendapatkan Step 1
Unit untuk AC-6b contactor adalah dalam kVAR
FAT PFCB
  Setting ck ratio
  Set Circular mode
  Set Switching Sequence seperti yang direka bentuk
    1:1:1:1:1:1 …
    1:1:2:2:2:2 …
    1:1:2:2:4:4 …
    1:2:2:2:2:2 …
    1:2:4:4:4:4 …
    1:2:4:8:8:8 …

## Slide 20: Earthing untuk peralatan ict
IEC 30129 : Information technology — Telecommunications bonding networks for buildings and other structures
Akan rujuk L-S38 : Specification For ICT Networking System
Telecommunication Bonding Conductor (TBC)
Primary Bonding Bar (PBB) in Server Room or Main TCR

## Slide 21: Earthing
Tukar Main Equipotential Bonding kepada Main Protective Bonding pada Gambarajah Pendawaian Skematik MSB

## Slide 22: Nilai bacaan earth electrode resistance test
R for MSB < 3Ω
R for landed quarters <10Ω
R for high rise quarters <3Ω
R for N-E Standby Gen-Set < 20Ω
R for LPS < 10Ω
R for N-E Transformer <3Ω
R for N-E Transformer <3Ω
R for Telephone System <1Ω (Jika diminta oleh TMB)

## Slide 23: Lightning Protection System
25mm x 3mm Aluminium Tape as a Air Termination System
Site – ONLY non coastal area
Bimetallic Testing Joint (Al/Cu)
Dari Bimetallic Testing Joint ke Earth Chamber mesti guna 25mm x 3mm Copper Tape

## Slide 24: Anda tanya, saya tolong jawab

## Slide 25: Terima KAsih