## section 7
SECTION 7.0 SCHEDULE OF EQUIPMENT OFFERED
7.1 | GENERAL
The tenderer shall complete this Schedule of Technical Data for Equipment Offered as set out below. All information for, shall be given correctly and supported by copies of manufacturer’s published technical data for the equipment being offered.
The tenderer is required to supply all the information as stipulated below and must be specific with regards to the make or manufacturer of the equipment offered. The words "or approved equivalent" wherever stated by the tenderer shall be deem void.
NO. |  | ITEMS | JKR REQUIREMENT | CONTRACTOR’S OFFER
7.2 | POOL CIRCULATION PUMPS
7.2.1 |  | Electrical Pumpset
| a. | No. of pump offered | 3 (2 Duty ,1 Standby)
| b. | Manufacturer of pump | To state by tenderer
| c. | Model no. of pump | To state by tenderer
| d. | Country of Origin | To state by tenderer
| e. | Type of pump | Centrifugal End Suction
| f. | Total Pump Head (ft) | 90
| g. | Flow Rate (Igpm) | 620
| h. | Max. pumping power | To state by tenderer
| i. | Efficiency of pump at specific condition | min 70%
| j. | NPSHr of pump at specific condition | max 10 ft
| k. | Pump Speed (RPM) | 1450
| l. | Pump NPSH & performance curve | Required (to be enclosed with pump brochure)
| m. | Pump overall dimension (LxWxH) | To state by tenderer
| n. | Operating pump weight | To state by tenderer
7.2.2 |  | Material of pump:
| a. | Casing | To state by tenderer
| b. | Impeller | Bronze/Stainless Steel
| c. | Shaft | Stainless Steel
| d. | Seal | Mechanical
7.2.3 |  | Pump Electric Motor:
| a. | Manufacturer and model | To state by tenderer
| b. | Type | TEFC
| c. | Insulation class | F
| d. | Rated (kW) | To state by tenderer
| e. | Starting Current (A) | To state by tenderer
| f. | Volts/Phase/Hz | To state by tenderer
7.2.4 |  | Motor Electric Stater:
| a. | Make and model no. | To state by tenderer
| b. | Type | To state by tenderer
| c. | Rated kW | To state by tenderer
| d. | Provide inertia block/motor base | Yes
| e. | Attached pump test certification | Yes
7.2.5 |  | Pump Switchboard
| a. | Make and manufacturer | To state by tenderer
| b. | Material/gauge of switchboard | To state by tenderer
| c. | Size of cubicle (mm) | To state by tenderer
| d. | Thickness of metal sheet (mm) | To state by tenderer
| e. | Catalogues and circuit diagram enclosed | Yes
| f. | Current consumption (A) | To state by tenderer
| g. | Operating Voltage(V) | To state by tenderer
| h. | Timer model | To state by tenderer
| i. | Relay model | To state by tenderer
| j. | Attached pump switchboard test certification | Yes
7.3 | SAND FILTER
7.3.1 |  | Sand Filter
| a. | Quantity provided | 3
| b. | Manufacturer | To state by tenderer
| c. | Country of Origin | To state by tenderer
| d. | Model | To state by tenderer
| e. | Type | To state by tenderer
| f. | Filtration rate | To state by tenderer
| g. | Diameter of each filter | To state by tenderer
| h. | Material of filter casing | To state by tenderer
| i. | Overall height (mm) | To state by tenderer
| j. | Overall width (mm) | To state by tenderer
| k. | Overall length (mm) | To state by tenderer
| l. | Unladen weight (kg) | To state by tenderer
| m. | Inlet/outlet size (dia. mm) | To state by tenderer
| n. | Filter area (m2) (each) | To state by tenderer
| o. | Max. working pressure (kg/cm2) | 2.5
| p. | Media grade (mm) (course/fine) | To state by tenderer
| q. | Media weight (kg) | To state by tenderer
| r. | Grain size | To state by tenderer
| s. | Maximum flow (igpm) (each) | 417
| t. | Conforming standard (attach certificate) | To state by tenderer
7.3.2 |  | Multiport Valve
| a. | Quantity provided | 3
| b. | Manufacturer | To state by tenderer
| c. | Country of Origin | To state by tenderer
| d. | Model | To state by tenderer
| e. | Type | Manual, Side mounted
| f. | Material of body | To state by tenderer
| g. | Valve function | 6-way
| h. | Inlet/outlet size (dia. mm) | To state by tenderer
| i. | Conforming standard (attach certificate) | To state by tenderer
| j. | Catalogues | Yes
7.4 | PIPING WORKS
7.4.1 |  | Piping
Above ground
| a. | Manufacturer of pipes | To state by tenderer
| b. | Class of pipe | E
| c. | Material of pipe | uPVC
| d. | Conforming standard (attach certificate) | Yes
7.4.2 |  | Under ground
| a. | Manufacturer of pipes | To state by tenderer
| b. | Class of pipe | E
| c. | Material of pipe | uPVC
| d. | Conforming standard (attach certificate) | Yes
7.4.3 |  | Type of Pipe Jointing
Above ground
| a. | Jointing Type | To state by tenderer
| b. | Material of jointing | To state by tenderer
| c. | Rated working pressure | To state by tenderer
| d. | Conforming standard (attach certificate) | Yes
7.4.4 |  | Underground
| a. | Jointing Type | To state by tenderer
| b. | Material of jointing | To state by tenderer
| c. | Rated working pressure | To state by tenderer
| d. | Conforming standard (attach certificate) | Yes
7.5 | VALVES AND FITTINGS
7.5.1 |  | Butterfly Valve
| a. | Make/model | To state by tenderer
| b. | Material of body | Cast Iron
| c. | Material of Disc | Stainless Steel
| d. | Material of spindle | Stainless Steel
| e. | Conforming standard (attach certificate) | Yes
7.5.2 |  | Check Valve
| a. | Make/model | To state by tenderer
| b. | Type | Flanged
| c. | Material of body | To state by tenderer
| d. | Material of valves | To state by tenderer
| e. | Conforming standard (attach certificate) | Yes
7.5.3 |  | Gate Valve
| a. | Make/model | To state by tenderer
| b. | Type | Full bore
| c. | Material of body | To state by tenderer
| d. | Material of valves | To state by tenderer
| e. | Conforming standard (attach certificate) | Yes
7.5.4 |  | Foot Valve
| a. | Make/model | To state by tenderer
| b. | Type | Flanged
| c. | Material of body | Stainless Steel
| d. | Material of seat/disc | Stainless Steel
| e. | Size (DN) | 200
7.5.5 |  | Hair & Lint Strainer
| a. | Make and model | To state by tenderer
| b. | Type | Stainless Steel
| c. | Material of body | Stainless Steel
| d. | Material of basket screen | Stainless Steel
7.5.6 |  | Sight Glass
| a. | Make and model no. | To state by tenderer
| b. | Type of glass | To state by tenderer
| c. | Size ( diameter & length ) | To state by tenderer
| d. | Conforming standard (attach certificate) | Yes
7.5.7 |  | Flow Meter
| a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Country of origin | To state by tenderer
| d. | Type | Electromagnetic
| e. | GPM range | To state by tenderer
| f. | Pressure ratings | To state by tenderer
| g. | Size offered (mm) | 200
| h. | Accuracy | +-0.5%
| i. | Material - Electrode | Stainless Steel 316
| j. | Material - Housing | Stainless Steel 316
| k. | Material - Liner | PTFE
| l. | Conforming standard (attach certificate) | Yes
7.5.8 |  | Other Fittings
| a. | Pressure gauge (Make and Type) | To state by tenderer
| b. | Conforming standard (attach certificate) | Yes
| c. | Flexible coupling (Make and Type) | To state by tenderer
| d. | Conforming standard (attach certificate) | Yes
| e. | Spring vibration isolator (Make and Type) | To state by tenderer
7.6 | POOL DISINFECTION SYSTEM
7.6.1 |  | Dosing Pump
| a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Quantity provided (nos.) | 4
| d. | Flow rate (liter/hour) | 14
| e. | Pressure (bar) | To state by tenderer
| f. | Input Power | To state by tenderer
7.6.2 |  | Chemical Tank
| a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Quantity provided (nos.) | 4
| d. | Capacity (liter) | 1000
7.6.3 |  | Automatic Chemical Regulator System
| a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Sensors | pH, Cl, ORP
| d. | Inputs | To state by tenderer
| e. | Outputs | To state by tenderer
| f. | Panel Size (mm) | To state by tenderer
7.7 | POOL UNDERWATER LIGHTING
| a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Quantity provided (nos.) | 12
| d. | Type | LED
| e. | Casing material | Stainless Steel
| f. | Rated Voltage | To state by tenderer
| g. | Protection | To state by tenderer
| h. | Lumens | To state by tenderer
| i. | Power Consumption (kW) | To state by tenderer
7.8 | POOL CLEANING ACCESSORIES
1 |  | Mobile Self-Priming Pumpset-Electric Motor
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Type/Model | To state by tenderer
| d. | Nameplate power (kW) | To state by tenderer
| e. | Speed (Rpm) | To state by tenderer
| f. | Full load current (Amp) | To state by tenderer
| g. | Starting current (Amp) | To state by tenderer
| h. | Efficiency at full load | To state by tenderer
2 |  | Pump
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Type/Model | To state by tenderer
| d. | Flow Rate (I/s) | To state by tenderer
| e. | Pressure Head (m) | To state by tenderer
3 |  | Trolley
| a. | Type | To state by tenderer
| b. | Material | To state by tenderer
4 |  | Floating Hose
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Length (m) | To state by tenderer
| d. | Reel diameter (mm) | To state by tenderer
| e. | Material | To state by tenderer
5 |  | Vacuum Head
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Material | To state by tenderer
6 |  | Adjustable Telescopic Pole
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Type/Model | To state by tenderer
| d. | Length (m) | To state by tenderer
7 |  | Leaf Rake
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Material | To state by tenderer
| d. | Type/Model | To state by tenderer
| e. | Size (W x L x H) mm | To state by tenderer
8 |  | Pool Brush
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Material | To state by tenderer
| d. | Type/Model | To state by tenderer
9 |  | Algae Brush
| a. | Manufacturer | To state by tenderer
| b. | Country of Origin | To state by tenderer
| c. | Material | To state by tenderer
| d. | Type/Model | To state by tenderer
7.9 | SUBMERSIBLE PUMP SYSTEM (PLANT ROOM)
7.9.1 | a. | Manufacturer | To state by tenderer
| b. | Model | To state by tenderer
| c. | Type of pump | Submersible
| d. | Pumping capacity | 55 igpm @ 30ft head
| e. | Rated Power (kW) | To state by tenderer
| f. | Efficiency of pump | To state by tenderer
| g. | Pump Speed (RPM) | To state by tenderer
| h. | Material of pump:
| i. | Casing | Stainless Steel
| j. | Impeller | Stainless Steel
| k. | Shaft | Stainless Steel
| l. | Seal | To state by tenderer