## Page 1
| CAWANGAN KEJURUTERAAN ELEKTRIK | [11 empty] | FORM NO : JKR.RCCB
| JKR MALAYSIA | [11 empty] | Sheet of
Record of RCCB Test
(For general purpose non-delayed type RCCB to IEC 1008)
A. PARTICULARS OF THE INSTALLATION [Please tick (√ ) the relevant boxes]
Project Name
Drawing No./Installation Address
Block No./Floor
DB Designation | [10 empty] | Phase:
B. TEST INSTRUMENT USED
Instrument |  | Brand |  | Model No. |  |  |  | Serial No. |  |  |  |  | Calibration Date
RCCB Tester
C. PARTICULARS OF THE RCCB (Please [√] the relevant box)
Rated Current (In) | [8 empty] | Brand |  |  |  | Model No.
D. TEST RESULTS (PLEASE X WHERE NOT APPLICABLE. PLEASE REFER TO PAGE 2 FOR TEST PROCEDURE)
Circuit No. | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
Circuit Reference
Mark S for Socket and L for Lighting. Others (specify)
Number of Points
RCCB Rated Tripping Current (mA)
TEST |  |  |  |  | Note | bar: 1 to 12
| RCCB Test Button |  |  |  | (i)
(Mark T for Trip & NT for No Trip)
| ½ I Trip |  |  |  | (ii)
(Mark T for Trip & NT for No Trip)
RCCB | I Trip at 0⁰ |  | (ms) |  | (iii)
Trip | I Trip at 180⁰ |  | (ms) |  | (iii)
Time | 5I Trip at 0⁰ |  | (ms) (if applicable) |  | (iv)
at | 5I Trip at 180⁰ |  | (ms) (if applicable) |  | (iv)
RCCB Test Button
(after completion of the above tests) |  |  |  |  | (v)
(Mark T for Trip and NT for No Trip)
RCCB Trip Current Test (RAmp Test) (mA) |  |  |  |  | (vi)
E. COMMENTS BY JKR (IF ANY) AND DEPARTURES FROM SPECIFICATION & REGULATIONS
F. PENGAKUAN ORANG KOMPETEN | [5 empty] | 2: G. PENGESAHAN JABATAN
( BAGI PIHAK KONTRAKTOR ELEKTRIK )
Diuji oleh: | [5 empty] | 2: Disaksi oleh:
| (Nama Pendawai) |  |  |  |  | 4: (Nama)
Tandatangan: | [5 empty] | 2: Tandatangan:
No. Kekompetenan: | [5 empty] | 2: Jawatan:
Tarikh Ujian: | [5 empty] | 2: Tarikh:
Nama & Cop Kontraktor:
mri/ra/wan/johor/MAC2008
Page 1 of 2
Single phase
3 phase
R
Y
B
63 A DP
63 A 4P
40A DP
40A 4P

## Page 2
CAWANGAN KEJURUTERAAN ELEKTRIK |  | FORM NO : JKR.RCCB
JKR MALAYSIA
Record of RCCB Test
(For general purpose non-delayed type RCCB to IEC 1008)
Note:
(i) | RCCB Test Button
The RCCB should be operated first by the test button to check that the RCCB is not faulty before
tests on the installation are made.
The test button does not test the circuit, protective conductors or any earthing conductors or earth.
The test button is to ensure that the electrical and mechanical elements of the RCCB are functioning.
(ii) | ½ I Test:
A test at ½ (50%) of the rated tripping current of the RCCB for a period of two (2) seconds.
This acts as a 'no trip' test and the RCCB must not trip. This is intended to verify that the RCCB is
not subject to tripping when spurious 'nuisance' current appear in the circuit being protected.
(iii) | I Test:
A Test at 100% of rated tripping current of the RCCB.
This act as a 'trip' test and the RCCB must break t he circuit within 300ms.
The choice of polarity, 0⁰ and 180⁰ enables the trip time to be measured accurately, as some RCCBs
performs differently if the current occurs at the beginning of a positive (0⁰) or a negative (180⁰)cycle.
(iv) | 5I Trip Test.
This test mainly for RCCBs rated at not more than 30mA (ie. 30mA & 10mA). The RCCB must break
the circuit within 40ms. The choice of polarity, 0⁰ and 180⁰ enables the trip to be measured
accurately, as some RCCBs performs differently if the current occurs at the beginning of a
positive (0⁰) or a negative (180⁰) cycle.
(v) | RCCB Test Button
Having completed the test, the effectiveness of the test button on the RCCB should again be
checked to ensure that everything is satisfactory.
vi) | RCCB Ramp Test
This test is to measure the trip current of an RCCB. Current level is slowly increase from half the
rated tripping current (0.5 x IΔn) of the RCCB. When the RCCB trips, the actual trip current
(in milliamps)displayed. Very useful diagnosing nuisance tripping of RCCB. RCCBs complying with
IEC 1008 may operate within the range of 0.5 to 1.0 x rated tripping current of the RCCB. If the RCCB
trips less than 0.5 x rated tripping current, replace the RCCB.
mri/ra/wan/johor/MAC2008
Page 2 of 2